Proactive sewer asset management in relation to groundwater infiltration using geospatial technology

Gestion proactive des actifs d’assainissement en relation avec l’infiltration d’eaux souterraines grâce à la technologie géospatiale

Nejat Zeydalinejad1, Akbar A. Javadi2, Mark Jacob3, David Baldock3, James L. Webber2

1 Centre for Resilience in Environment, Water and Waste (CREWW), University of Exeter, North Park Road, Exeter EX4 4TA, UK (N.Zeydalinejad@exeter.ac.uk)

2 Centre for Water Systems, Department of Engineering, Faculty of Environment, Science and Economy, University of Exeter, North Park Road, Exeter EX4 4QF, UK (A.A.Javadi@exeter.ac.uk and J.Webber2@exeter.ac.uk)

3 South West Water, Peninsula House, Rydon Lane, Exeter EX2 7HR, UK (mjacob@southwestwater.co.uk and dbaldock@southwestwater.co.uk)

# RÉSUMÉ

Les systèmes d’égouts constituent des éléments essentiels de l’infrastructure urbaine, influençant les résultats environnementaux, sociaux et économiques. Cependant, ces systèmes sont soumis à des pressions croissantes liées au changement climatique, au vieillissement des actifs, à l’expansion urbaine et à l’augmentation des apports d’eaux parasites. L’infiltration des eaux souterraines dans les réseaux d’égouts, l’un des facteurs de stress les plus importants, accroît les coûts d’exploitation, réduit la capacité hydraulique et contribue aux déversements d’eaux pluviales, entre autres défis. La modélisation de l’infiltration des eaux souterraines dans les réseaux d’égouts est non seulement longue et complexe, mais elle nécessite également des données hydrologiques et patrimoniales étendues, qui sont souvent indisponibles. Il existe donc un besoin évident de méthodes plus simples et plus économes en ressources pour hiérarchiser ces risques. Ici, une approche géospatiale est utilisée pour calculer des scores de risque d’infiltration des eaux souterraines sur une étude de cas sélectionnée, à une résolution spatiale de 1 m², en combinant plusieurs jeux de données proxy disponibles. Les résultats aident les compagnies des eaux à prioriser l’inspection, la maintenance et la réhabilitation dans l’ensemble de leurs réseaux. La comparaison avec les données observées de déversements d’eaux pluviales démontre l’applicabilité pratique de l’approche, soutenant une gestion proactive des actifs, l’optimisation des opérations et le renforcement de la résilience à long terme face aux pressions du changement climatique et de l’urbanisation.

# ABSTRACT

Sewer systems are critical components of urban infrastructure, influencing environmental, social, and economic outcomes. However, these systems face increasing pressures from climate change, ageing assets, urban expansion and rising inflow and infiltration. Groundwater infiltration into sewer networks, as one of the most significant existing stresses, exacerbates operational costs, reduces hydraulic capacity, and contributes to storm overflow events, among other challenges. Modelling groundwater infiltration in sewer networks is not only time-consuming and challenging but also requires extensive hydrological and asset data, which are often unavailable. There is therefore a clear need for more straightforward and resource-efficient approaches to triage these risks. Here, a geospatial approach is employed to compute groundwater infiltration risk scores over a selected case study at 1 m2 spatial resolution by combining multiple available proxy data sets. Findings assist water companies in prioritising inspection, maintenance, and rehabilitation across their networks. Comparison with observed storm overflow data demonstrates the practical applicability of the approach, supporting proactive asset management, optimising operations, and enhancing long-term resilience under climate change and urbanisation pressures.

# KEYWORDS

Asset management, Sewer networks, Groundwater infiltration, Urban resilience, Water companies

# Introduction

The growing challenges of climate change, urbanisation, and shifts in the hydrological cycle pose escalating threats to groundwater and relevant subsurface infrastructure, including groundwater infiltration (GWI) in sewer networks (Zeydalinejad et al., 2025a, b). GWI refers to the movement of groundwater into the pipes through cracks, faulty joints, and other imperfections (Pangle et al., 2022). GWI to the sewer network reduces capacities of existing infrastructure, potentially leading to increased treatment costs and risks of environmental discharges (Zeydalinejad et al., 2024a, b). It can lead to accelerated and prolonged activation of combined sewer overflows (CSOs) and the risk of drainage pipe collapse (Zhang et al., 2018). GWI can also significantly disrupt the hydrological cycle in urban and suburban areas (Pangle et al., 2022).

Water companies are increasingly taking proactive measures to assess the maintenance needs of pipes where GWI may pose a risk. However, current prioritisation methodologies often rely on limited data sets or are driven by tactical operational requirements, such as reactive site investigations, which can be inefficient for large-scale network management. Therefore, exploring strategies to improve strategic planning is essential, such as leveraging geospatial technology to map GWI hotspots.

Indeed, to mitigate the aforementioned environmental impacts, the development of new methods for catchment monitoring and evaluation has become critical (Tavosi et al., 2024). One of the most frequently employed tools in this perspective is prioritisation, which has become increasingly significant in effective natural resource management and the pursuit of sustainable development, under the pressure of constrained time and resources (Priya, 2023).

Assessing GWI in sewer networks is essential for protecting infrastructure and addressing operational challenges. Yet, despite its importance, relatively few studies have investigated this issue. The primary aim of this study is to establish a comprehensive framework for evaluating GWI risk by generating probability scores (ranging from 0 to 1) and identifying the key influencing factors. Specifically, we estimate GWI probability scores within sewer systems using a fuzzy (F)–analytical hierarchy process (AHP)–geographic information system (GIS) framework to derive GWI prioritisation scores.

# Materials and methods

## Methods

The F-AHP within a GIS framework was employed, considering geology, geomorphology, hydrology, hydrogeology, climate, and topography. The model comprised 16 thematic layers: groundwater depth (GWD), elevation, slope, topographic wetness index (TWI), precipitation, rock, alluvium, soil type, land cover (LC), made ground, fault proximity, fault length, mass movement, river proximity, flood potential, and drainage order. Expert judgement, fuzzy analysis, and AHP were applied for layer classification, normalisation (i.e. scaling values between 0 and 1), and weight assignment, respectively.

The proposed methodology was verified to ensure robustness and reliability. The Consistency Ratio (CR) was used to assess the AHP component within the GIS framework, with values below 0.10 indicating high consistency in pairwise comparisons. In addition, a sensitivity analysis was performed to evaluate the influence of individual thematic layers on final risk scores, ensuring the model’s reliability and identifying the most critical factors affecting GWI.

## Study area

In this research, we investigated a semi-urbanised catchment in the South West of the United Kingdom. The catchment includes both urban and rural land uses spanning across approximately 138 km2. This is typical of a medium sized sewer catchment in the South West of England. The distribution of sewer networks and sewersheds is primarily concentrated in the southeastern, and northern parts of the study area (Figure 1).

Fig. 1 Location of the study area (a), key features (b), and GWI prioritisation scores (c)

# Results

Pairwise comparisons for deriving layer weights were calculated to achieve a CR of 0.02, demonstrating a consistent and robust F-AHP integration. The resulting weights were : GWD=13.45, river proximity=10.8, rock=8.75, alluvium=8.30, flood potential=8, fault proximity=6.8, fault length=6.8, TWI=6.4, made ground=5.05, soil type=4.55, slope=4.4, LC=4, mass movement=3.45, drainage order=3.2, elevation=3.05, and precipitation=3. This identified GWD, river proximity, rock type, alluvium presence and flood potential as the primary influencing factors on GWI priortisation.

The integration of all layers using the F-AHP–GIS framework produced GWI probability scores for each 1 m² cell, with values ranging from 0.13 to 0.65. The highest GWI prioritisation scores were identified in the northeast of the study area. This was commensurate with proximity to low lying land approaching an estuary.

It is noteworthy that locations showing increased storm overflow discharges (identified using open source reporting) largely coincided with areas showing higher GWI probabilities. This mainly occurred in low-lying zones with gentle slopes and close to rivers with higher flood potential (Figure 1). This correlation supports an initial thesis that GWI may be playing an important role in taking up network capacity and making CSO spills more likely. Understanding the scale and likelihood of potential additional inflows to the sewer system is of particular importance given water company efforts to reduce these spill events.

# discussion

Data imperfections, such as gaps, outliers, and imbalanced data sets, are significant challenges in studies assessing sewer network failure risks (Fontecha et al., 2021). While surveys of infrastructure focusing on vulnerable sewer mains are often carried out for risk management purposes, an ideal survey for modelling and predicting conditions would involve a representative sample from all types of assets (Mashford et al., 2011). Herein, rather than constructing a physics-based groundwater model coupled with a sewer network approach, which requires considerable effort and detailed hydrogeological and asset data, we integrated available proxies into a geospatial framework that is highly efficient both in terms of time and computation.

Given the constraints of budget, time, and available assessment tools, conducting comprehensive monitoring and inspections across all sewer pipelines is practically unfeasible. Moreover, applying traditional methodologies across an entire sewer network demands significant financial resources and time. The underground nature of sewer infrastructure, coupled with the high costs associated with closed-circuit television (CCTV) inspections and the severe consequences of pipeline failures, underscores the necessity for advanced techniques to evaluate failure risks and optimise inspection priorities. In this context, the outputs of our GIS-based model offer practical applications by identifying high-risk zones, guiding targeted inspections, and supporting evidence-based prioritisation of maintenance and mitigation measures (Zeydalinejad et al., 2025a).

By focusing on zones with higher GWI prioritisation scores, South West Water (SWW) can optimise its resources by targeting areas most likely to experience infiltration, reducing unnecessary investigations in low-risk zones, supporting long-term maintenance and inspection planning, and helping to prevent future issues.

# Conclusions

Overall, this study highlights the effectiveness of the proposed F-AHP-based GIS approach for assessing GWI in sewer networks. The resulting framework equips asset managers with a practical tool for prioritising engineering actions to support long-term asset sustainability. It delivers high-resolution (1 m × 1 m) GWI probability scores covering both current sewered zones and locations where future infrastructure may be installed. The value of this work lies in providing a transferable, data-driven approach that improves GWI estimation and enables proactive, informed decision-making, thereby enhancing the resilience and sustainability of urban water systems.

# LIST OF REFERENCES

Fontecha, J.E., Agarwal, P., Torres, M.N., Mukherjee, S., Walteros, J.L. and Rodríguez, J.P. (2021). A two-stage data-driven spatiotemporal analysis to predict failure risk of urban sewer systems leveraging machine learning algorithms. Risk Anal., 41, 2356–2391.

Mashford, J., Marlow, D., Tran, D. and May, R. (2011). Prediction of sewer condition grade using support vector machines. J. Comput. Civ. Eng., 25, 283–290.

Pangle, L.A., Diem, J.E., Milligan, R., Adams, E. and Murray, A. (2022). Contextualizing inflow and infiltration within the streamflow regime of urban watersheds. Water Resour. Res., 58, e2021WR030406.

Priya, K. (2023). Sub-watershed prioritization of Kariangote River in Kerala based on drainage morphometry and geomorphology – a remote sensing and GIS approach. Indian J. Sci. Technol., 16, 978–988.

Tavosi, M., Vafakhah, M., Sadeghi, S.H. and Bateni, S.M. (2024). Sub-watershed prioritization based on watershed hydrological security using different multi-criteria decision-making methods. Water Resour. Manag., 1–26.

Zeydalinejad, N., Javadi, A.A., Baldock, D. and Webber, J.L. (2024b). An integrated hydrological-hydrogeological model for analysing spatio-temporal probability of groundwater infiltration in urban infrastructure. Sustainable Cities Soc., 116, 105891.

Zeydalinejad, N., Javadi, A.A. and Webber, J.L. (2024a). Global perspectives on groundwater infiltration to sewer networks: A threat to urban sustainability. Water Res., 262, 122098.

Zeydalinejad, N., Javadi, A.A., Jacob, M., Baldock, D. and Webber, J.L. (2025a). Can Proxy-Based Geospatial and Machine Learning Approaches Map Sewer Network Exposure to Groundwater Infiltration? Smart Cities, 8(5), 145.

Zeydalinejad, N., Javadi, A.A., Jacob, M., Baldock, D. and Webber, J.L. (2025b). Prioritising sewersheds based on groundwater infiltration probability: A geospatial approach. Water Res., 124521.

Zhang, M., Liu, Y., Cheng, X., Zhu, D.Z., Shi, H. and Yuan, Z. (2018). Quantifying rainfall-derived inflow and infiltration in sanitary sewer systems based on conductivity monitoring. J. Hydrol., 558, 174–183.