A QGIS Plugin to reconcile topological inconsistencies in sewer networks for hydraulic modelling and prioritize field verifications

Un plugin QGIS pour corriger les incohérences topologiques dans les réseaux d’assainissement pour la modélisation hydraulique et prioriser les vérifications de terrain

Sílvia Busquets1,2; Josep Pueyo1, Lluís Corominas1, Lluís Ayach2, Xavier Oliva2

sbusquets@icra.cat; jpueyo@icra.cat; lcorominas@icra.cat

1Catalan Institute for Water Research (ICRA), Girona (Spain)

2Tractament de Residus i d'Aigües Residuals del Sistema de Girona (TRARGISA), S.A., Girona (Spain)

# RÉSUMÉ

La gestion des eaux pluviales urbaines représente un défi majeur en urbanisme et joue un rôle central dans la politique environnementale européenne. Dans ce contexte, les services publics de l’eau européens doivent évaluer la performance hydraulique de leurs réseaux d’assainissement. En général, cette évaluation repose sur des inventaires basés sur les SIG, qui contiennent souvent des incohérences topologiques et des informations manquantes. Différentes méthodologies ont été proposées pour résoudre ces problèmes ; toutefois, aucune n’est entièrement compatible avec les flux de travail et les logiciels couramment utilisés par les services publics de l’eau.

Nous présentons ici un flux de travail et les modules d’un plugin QGIS conçu pour corriger les données des réseaux d’assainissement et préparer les systèmes pour la modélisation hydraulique. Les résultats préliminaires montrent que le plugin peut identifier les conduits dont la direction est incorrecte, vérifier les éléments physiques connectés à la station d’épuration et compléter les attributs manquants des jonctions, tels que l’altitude du fond de canalisation. Cette fonctionnalité permettra aux services publics de l’eau de réduire significativement le temps consacré à la correction des données réseau et de disposer de systèmes d’assainissement prêts à être intégrés dans leur logiciel SIG, les préparant ainsi pour le modèle hydraulique.

# ABSTRACT

Urban stormwater management represents a significant challenge in city planning and plays a central role in European environmental policy. In this context, European water utilities need to assess the hydraulic performance of their sewer systems. Typically, this assessment relies on GIS-based inventories, which often contain topological inconsistencies and missing information. Different methodologies have been proposed to address these issues; however, none are fully compatible with the workflows and software that water utilities commonly use.

Here, we present a workflow and the modules of a QGIS plugin designed to correct sewer network topology to facilitate hydraulic modelling. Preliminary results show that the plugin can automatically identify and automatically correct conduits with wrong flow direction, check the junctions and conduits connected to the wastewater treatment plant, and fill in the missing attributes of junctions, such as invert elevation. This functionality will allow water utilities to significantly reduce the time spent correcting network data and to have sewer systems ready for integration into their GIS software, making them prepared for the hydraulic modelling exercise.

# KEYWORDS

Data correction and modelling, GIS-based inventory, graph theory, hydraulic modelling, QGIS plugin

# INTRODUCTION

Urban stormwater management is a challenge in city planning and is increasingly reflected in public policy, emphasizing the urgent need for adaptation to climate change. At the same time, urban wastewater management is central to European environmental policy: the new Wastewater Treatment Directive (2024/3019) mandates that water utilities assess the hydraulic performance of their urban drainage systems (UDS). Although these networks are usually maintained in Computer-Aided Design (CAD) or vector formats within Geographic Information Systems (GIS), they often contain topological inconsistencies that must be corrected for hydraulic models. In the process of correcting and updating network assets, key elements that would ensure a sufficiently robust network for reliable modelling are not always prioritized. Furthermore, a survey that we sent out to practitioners and researchers showed that 81% of the respondents usually performed the data reconciliation process semi-automatically using software tools that facilitate this task. Although it is a semi-automatic method, the number of hours to carry out this work reaches 20 hours for 41% of respondents while 32%, 20 to 50 hours.

Different methodologies have been used to complete and correct sewer networks. Shao et al., (2017) employed SWMM-based algorithm to design storm sewer network; however, their approach relied only on iterative hydraulic calculations without incorporating real sewer network data. Belghaddar et al., (2021) used Graph Convolutional Network models to complete missing values of pipes by leveraging network topology and the relationship between components. This approach, however, needs a large set of data for training. Graph theory has also been widely applied in UDS. Meijer et al., (2018) used this method to identify the most critical elements in a network with respect to malfunctioning of the system. Chegini & Li, (2022) combined graph theory with available land surface data, topography, and land use/land cover to construct urban stormwater networks. More recently, Hajibabaei et al., (2025) implemented automated graph theory approach for data collection and network reconstruction to fill gaps in UDS. Although the mentioned methods provide frameworks for reconstructing sewer networks, none of them offer user-friendly workflows that water utilities can readily apply. To ensure seamless integration into existing GIS workflows, we present a plugin for the open-source GIS desktop software QGIS. The plugin enables the correction of sewer networks, including checking the junctions and conduits connected to the wastewater treatment plant, conduit directions and missing attributes such as invert and manhole elevations, by applying graph theory. It also allows the generation of vector files containing both the corrected elements and those prioritized for field verification, and the creation of a hydrological model of the sewer system.

# OBJECTIVE

The aim of this work is to introduce the workflow and the designed QGIS plugin to correct sewer networks for hydraulic modelling and to present the preliminary results of its application.

# METHODOLOGY

The objective of this plugin is to reduce the time required to prepare sewer networks for hydraulic modelling. We demonstrate its applicability using the UDS of Girona (Spain) as a case study.  The UDS of Girona consists of 660 kilometres of network with 205000 population equivalents connected, which fluctuates seasonally due to the tourism. The inventory of UDS used to be maintained in CAD format. Recently, the water utility has been adopted its inventory in GISwater database format. GISwater is a free open-source software designed for the integrated management of water cycle, acting as a link between hydraulic analysis tools and spatial database. The maintenance and database update process currently involves only one person and is performed only when big changes in the UDS are produced (i.e. civil engineering works).

The plugin was initially implemented in the Python programming language and subsequently adapted for integration into QGIS. Figure 1 shows the workflow of the plugin which starts with the UDS as input. It supports the most common network inventory formats: vector files, INP files and database connections (e.g., PostgreSQL). The plugin comprises four modules: the first, A, “Generate SWMM INP” converts the input data to a Geopackage in the case it is an INP file or a database; the second, B, the “UD Correction Module”, uses graph theory to check flow directions and cycles, fill in missing values, and detect or prevent SWMM errors; the third, C,  “Generate SWMM INP module”, converts the Geopackage into an INP file for simulation; and the fourth, D,”SWMM API”, runs the model simulation using the SWMM API. Module B generates two outputs: vector files containing corrected and uncorrected conduits, and a prioritized list of elements for field verification. Module D produces a status report from the simulation. If the simulation results are unsatisfactory, the user can inspect the prioritized elements in the field to complete the inventory, after which the workflow can be repeated.

Figure 1. Workflow of the plugin and its modules

# PRELIMINARY RESULTS

Some key preliminary results of module B are presented. The urban drainage system of Girona consists of 14303 junctions and 14458 conduits. The components connected to the wastewater treatment plant (junctions and conduits) were 12683 and 13203, respectively. Before running the plugin, 3129 junctions lacked invert elevation, which were automatically filled (Figure 2, left). Note that invert elevation is crucial for slope calculation in hydraulic modelling.

Figure 2. Left: Junctions shown in yellow indicate missing invert elevations that were automatically filled using the plugin. Right: One of loops detected in the network.

Four loops were detected in the network, which is important to identify to prevent the interruption of indicator propagation (Figure 2, right). Moreover, 3307 conduits were adjusted to prevent SWMM error 112, with the plugin providing 19 of these for field verification. During the reconciliation process, the algorithm detected incorrect conduit directions. Figure 3 shows an example: one conduit was oriented opposite to the flow direction toward the Wastewater Treatment Plant (WWTP), which resulted in part of the network being affected.

Figure 3. Left: in pink, the junctions and conduits of the area connected to the incorrectly directed conduit. Right: the conduit with a flow direction opposite to that of the WWTP.

These results are preliminary and refer to module B. The current work continues with the development and testing of the remaining modules. The next steps will involve validating the complete workflow on the main study city. Prior to this, the workflow will be tested on a smaller city to facilitate easier error checking and ensure reliability before full-scale application. Comprehensive results from the entire workflow will be available for presentation at the time of the conference.

# LIST OF REFERENCES

Belghaddar, Y., Chahinian, N., Seriai, A., Begdouri, A., Abdou, R., & Delenne, C. (2021). Graph convolutional networks: Application to database completion of wastewater networks. Water (Switzerland), 13(12). https://doi.org/10.3390/w13121681

Chegini, T., & Li, H. Y. (2022). An algorithm for deriving the topology of belowground urban stormwater networks. Hydrology and Earth System Sciences, 26(16), 4279–4300. https://doi.org/10.5194/hess-26-4279-2022

Hajibabaei, M., Hesarkazzazi, S., & Sitzenfrei, R. (2025). Filling data gaps in urban drainage networks: An automated graph theory framework for data collection and reconstruction. Water Research, 287. https://doi.org/10.1016/j.watres.2025.124272

Meijer, D., Bijnen, M. van, Langeveld, J., Korving, H., Post, J., & Clemens, F. (2018). Identifying critical elements in sewer networks using graph-theory. Water (Switzerland), 10(2). https://doi.org/10.3390/w10020136

Shao, Z., Zhang, X., Li, S., Deng, S., & Chai, H. (2017). A novel SWMM based algorithm application to storm sewer network design. Water (Switzerland), 9(10). https://doi.org/10.3390/w9100747